## Calculation Sheet
Community Development Department
Building and Safety Division
200 Old Bernal Avenue ¦ P.O. Box 520
Pleasanton, California 94566-0802
Phone 925-931-5300 ¦ www.pleasantonpermits.com
EXISTING DWELLING UNIT LOAD CALCULATION
|  | JOB ADDRESS: |  |  | PERMIT #:
|  | PREPARED BY: |  |  | DATE:
CONTACT PHONE:
|  | SERVICE/FEEDER AMPS: |  | Value for service/feeder must be provided.
QUANTITY | LOAD |  | MIN RATING |  | COLUMN 1 | COLUMN 2 | Common Values
| Dwelling square feet. |  | 3 x sq. ft. |  | 0
| Small appliance circuits (2 min.) |  | 1,500VA each |  | 0 |  | 1,500 ea.
| Laundry circuit (1 min.) |  | 1,500VA each |  | 0 |  | 1,500 ea.
| Dryer (5000 min or name plate rating) |  | 5,000VA minimum |  |  |  | 5000
| Electric oven(s) |  | Nameplate rating |  |  |  | 8000
| Electric cook top(s) |  | Nameplate rating |  |  |  | 8000
| Refrigerator |  | Nameplate rating |  |  |  | 1400
| Garbage disposal |  | Nameplate rating |  |  |  | 800
| Microwave |  | Nameplate rating |  |  |  | 1500
| Dishwasher |  | Nameplate rating |  |  |  | 1200
| Forced air unit |  | Nameplate rating |  |  |  | 1650
| Air conditioner(s)/ Heat Pumps(s) |  | Nameplate rating |  |  |  | 7200
| Pool equipment |  | Nameplate rating
| Individual space heating |  | Nameplate rating
| EV charger |  | Nameplate rating |  |  |  | 9600
| Jacuzzi tub |  | Nameplate rating |  |  |  | 12000
| Other: |  | Nameplate rating
| Other: |  | Nameplate rating
TOTAL WATTS: |  |  |  |  | 0 | 0
| First 8000 watts from Column 1 at 100%: |  |  | 8000
| (Column 1 total - 8,000) x 0.40%: |  |  | 0
| Column 2 Total at 100%: |  |  | 0
| TOTAL WATTS |  |  | 0
MINIMUM SERVICE REQUIRED (TOTAL WATTS / 240 V): |  |  |  | 0
SERVICE UPGRADE NOT REQUIRED
The above schedule is intended as a guide for those desiring to prepare their own plans. Because of varying conditions, details as shown may meet the requirements of the Electrical Code. See article 220.83 of the National Electrical Code for exact requirements.
REVISED 10/2024 JLA
Note on B19: 2022 CEC 220.83(A)(1) General lighting and general-use receptacles at 33 volt-amperes/m2 or 3 volt-amperes/ft2 as determined by 220.12
Note on B20: 2022 CEC 220.83(A)(2) 1500 volt-amperes for each 2-wire, 20-ampere small-appliance branch circuit. 2022 CEC 210.11(C)(1) (1) Small-Appliance Branch Circuits In addition to the number of branch circuits required by other parts of this section, two or more 20-ampere small-appliance branch circuits shall be provided for all receptacle outlets specified by 210.52(B).
Note on B21: 2022 CEC 220.83(A)(2) Each laundry branch circuit covered in 210.11(C)(1) and (C)(2). 2022 CEC 210.11(C)(2) (2) Laundry Branch Circuits In addition to the number of branch circuits required by other parts of this section, at least one additional 20-ampere branch circuit shall be provided to supply the laundry receptacle outlet(s) required by 210.52(F). This circuit shall have no other outlets.
Note on B22: 2022 CEC 220.83(A)(2) (2)1500 volt-amperes for each 2-wire, 20-ampere small-appliance branch circuit and each laundry branch circuit covered in 210.11(C)(1) and (C)(2) 220.54 Electric Clothes Dryers — Dwelling Unit(s) The load for household electric clothes dryers in a dwelling unit(s) shall be either 5000 watts (volt-amperes) or the nameplate rating, whichever is larger, for each dryer served. For more info regarding multiply dryer loads, see 2022 CEC 220.54.
Note on B23: 2022 CEC 220.83(A)(3)(b) The nameplate rating of the following: (b)Ranges, wall-mounted ovens, counter-mounted cooking units.
Note on B24: 2022 CEC 220.83(A)(3)(a) (a)The nameplate rating of the following: All appliances that are fastened in place, permanently connected, or located to be on a specific circuit.
Note on B25: 2022 CEC 220.83(A)(3)(a) (a)The nameplate rating of the following: All appliances that are fastened in place, permanently connected, or located to be on a specific circuit.
Note on B26: 2022 CEC 220.83(A)(3)(a) (a)The nameplate rating of the following: All appliances that are fastened in place, permanently connected, or located to be on a specific circuit.
Note on B27: 2022 CEC 220.83(A)(3)(a) (a)The nameplate rating of the following: All appliances that are fastened in place, permanently connected, or located to be on a specific circuit.
Note on B28: 2022 CEC 220.83(A)(3)(a) (a)The nameplate rating of the following: All appliances that are fastened in place, permanently connected, or located to be on a specific circuit.
Note on B29: 2022 CEC 220.83(A)(3)(a) (a)The nameplate rating of the following: All appliances that are fastened in place, permanently connected, or located to be on a specific circuit.
Note on B30: 2022 CEC 220.83(B) Air-conditioning equipment 100% of load, (no reduction factor can be applied to Air Condiutioner or Heat Pump load).
Note on B31: 2022 220.14(A) (A) Specific Appliances or Loads An outlet for a specific appliance or other load not covered in 220.14(B) through (M) shall be calculated based on the ampere rating of the appliance or load served. (Pool equipment is classified as equipment rather than an appliance. As such, no demand factor can be applied to pool equipment loads).
Note on B32: 2022 CEC 220.83(B) Central electric space heating load shall be applied 100%. 2022 CEC 220.51 Fixed Electric Space Heating Fixed electric space-heating loads shall be calculated at 100 percent of the total connected load. However, in no case shall a feeder or service load current rating be less than the rating of the largest branch circuit supplied. Exception: Where reduced loading of the conductors results from units operating on duty-cycle, intermittently, or from all units not operating at the same time, the authority having jurisdiction may grant permission for feeder and service conductors to have an ampacity less than 100 percent, provided the conductors have an ampacity for the load so determined.
Note on B33: 2022 220.14(A) (A) Specific Appliances or Loads An outlet for a specific appliance or other load not covered in 220.14(B) through (M) shall be calculated based on the ampere rating of the appliance or load served. (EV chargers is considered equipment rather than an appliance. As such, no demand factor can be applied to EV charger loads. Apply 100% of EV charger name plate rating).
Note on B34: 2022 220.14(A) (A) Specific Appliances or Loads An outlet for a specific appliance or other load not covered in 220.14(B) through (M) shall be calculated based on the ampere rating of the appliance or load served. (Pool equipment is classified as equipment rather than an appliance. As such, no demand factor can be applied to pool equipment loads).
Note on B39: 2022 CEC 220.83(A) or (B) The following percentages shall be used for existing and additional new loads. Load (kVA) Percent of Load First 8 kVA of load at 100 Remainder of load at 40
Note on B40: 2022 CEC 220.83(A) or (B) The following percentages shall be used for existing and additional new loads. Load (kVA) Percent of Load First 8 kVA of load at 100 Remainder of load at 40